## Лист1
Sbas, MVA | Ubas, kV
1000 | 340
1. Power lines
Unom, kV | S, mm2 | r0, Om/100 km | x0, Om/100 km | b0, 10-6 Sm/km | l, km | nl, p
330 | 300/39 | 4.8 | 32.8 | 341 | 50 | 2
Average nominal voltage, kV |  | R, Om | X, Om | B, 10-6 Sm
340 |  | 1.2 | 8.2 | 341
|  | Rline, pub | Xline, pub | Bline1 (Bline2), pub
|  | 0.010381 | 0.070934 | 0.01971
2. Transformers
Snom, MVA | Usc, % | ΔPsc, kW | Unom, kV | R, Om | X, Om | nt, p
200 | 11 | 560 | 347 | 0.84286 | 33.1125 | 2
|  |  |  | Rt, Om | Xt, Om
|  |  |  | 0.007 | 0.275
3. Synchronous machine
Pnom, MW | Ug nom, kV | cosφ nom, pu | n, rev/min | J, t*m2 | xd, pu | xq, pu | x'd, pu | x''d, pu | x''q, pu | xs, pu | Td0, s | T''d, s | T''q, s | Pg, MW | Qg, MVAr | ngen, p
200 | 15.75 | 0.85 | 3000 | 6.25 | 1.84 | 1.84 | 0.295 | 0.19 | 0.19 | 0.165 | 6.9 | 0.14 | 0.5 | 190 | 60 | 2
|  |  |  | Tj_p | xd_p, pub | xq_p, pub | x'd_p, pub | x''d_p, pub | x''q_p, pub | xs_p, pub | rf_p, pub | r1d_p, pub | r1q_p, pub | Pg, pub | Qg, pub
|  |  |  | 4.932 | 3.91 | 3.91 | 0.62687 | 0.40375 | 0.40375 | 0.35063 | 0.0017811 | 0.0050111 | 0.0021785 | 0.38 | 0.12
[5 empty] | xad | xaq | xsr | xsrd | xsrq
[5 empty] | 3.5594 | 3.5594 | 0.29949 | 0.065774 | 0.05393
4. Load
Pn, MW | Qn, MVAr | nl, p
30 | 5 | 2
Gn, pub | Bn, pub
0.06 | -0.01
Note on A1: Андрей: Basic power
Note on B1: Андрей: Basic phase-to-phase voltage
Note on A5: Андрей: nominal phase-to-phase line voltage
Note on B5: Андрей: nominal wire cross-section
Note on C5: Андрей: linear active line resistance
Note on D5: Андрей: linear active line resistance
Note on E5: Андрей: linear line capacitive conductivity
Note on F5: Андрей: line length
Note on G5: Андрей: number of lines
Note on A7: Андрей: taken from the scale of average nominal voltage
Note on C7: Андрей: active line resistance
Note on D7: Андрей: reactive line resistance
Note on E7: Андрей: line capacitive conductivity
Note on C9: Андрей: active line resistance
Note on D9: Андрей: reactive line resistance
Note on E9: Андрей: one half of line capacitive conductivity
Note on A13: Андрей: Nominal transformer power
Note on B13: Андрей: short circuit voltage
Note on C13: Андрей: loss of active power in case of short circuit
Note on D13: Андрей: nominal voltage of the high side of the transformer
Note on E13: Андрей: active transformer resistance
Note on F13: Андрей: reactive transformer resistance
Note on G13: Андрей: number of transformers
Note on E15: Андрей: active transformer resistance
Note on F15: Андрей: reactive transformer resistance
Note on A19: Андрей: Nominal generator power
Note on B19: Андрей: Nominal generator voltage
Note on C19: Андрей: nominal power factor
Note on D19: Андрей: rotor speed
Note on E19: Андрей: moment of inertia
Note on F19: Андрей: d-axis synchronous reactance
Note on G19: Андрей: q-axis synchronous reactance
Note on H19: Андрей: d-axis transient reactance
Note on I19: Андрей: d-axis subtransient reactance
Note on J19: Андрей: q-axis subtransient reactance
Note on K19: Андрей: leakage reactance
Note on L19: Андрей: d-axis transient time constant when the stator winding is open
Note on M19: Андрей: d-axis subtransient time constant when the stator winding is closed
Note on N19: Андрей: q-axis subtransient time constant when the stator winding is closed
Note on O19: Андрей: actual generation of active power
Note on P19: Андрей: actual generation of reactive power
Note on Q19: Андрей: number of generators
Note on E21: Андрей: inertia coefficient
Note on F21: Андрей: d-axis synchronous reactance
Note on G21: Андрей: q-axis synchronous reactance
Note on H21: Андрей: d-axis transient reactance
Note on I21: Андрей: d-axis subtransient reactance
Note on J21: Андрей: q-axis subtransient reactance
Note on K21: Андрей: leakage reactance
Note on L21: Андрей: active resistance of field winding
Note on M21: Андрей: active resistance of d-axis damper winding
Note on N21: Андрей: active resistance of q-axis damper winding
Note on O21: Андрей: actual generation of active power
Note on P21: Андрей: actual generation of reactive power
Note on A27: Андрей: active load of consumer
Note on B27: Андрей: reactive load of consumer
Note on C27: Андрей: number of consumers
Note on A29: Андрей: active conductivity
Note on B29: Андрей: reactive conductivity